## Sheet1
|  | pf | 0.7 | [6 empty] | Duty Cycle
|  | voltage | 220 | [6 empty] | SB | 0.7
[10 empty] | ST | 0.5
[10 empty] | S | 0.25
|  | Watts | Amp
| fan (F) | 100
https://waltonbd.com/led-light/indoor/office-light/led-surface-panel-light/wled-splr300-ul24w | ceiling light (CL) | 24
| tubelight (TL) | 45
https://waltonbd.com/led-light/indoor/residential-led-lights/led-bulbs/public-series | Light bulb (LB) | 20
| EF | 50
| Switch board Socket (SS) | 100 | 5
| Power socket 1 (ST) | 2000 | 15
| Power socket 2 (S) | 3000 | 20
Documentation
https://www.daftlogic.com/information-appliance-power-consumption.htm
18
Top Floor
|  | Fan | CL | TL | LB | EF | SS | power | CKT POWER | Current | CKT AMP | TOTAL SUM (SB) |  |  | TOTAL SUM (ESB)
| SB3 | 1 | 1 | 0 | 1 | 0 | 1 | 244 |  | 1.5844 | 0 | TOP FLOOR SB POWER | 3100 |  | TOP FLOOR | 2484
| SB4 | 0 | 0 | 0 | 1 | 1 | 1 | 170 | 514 | 1.1039 | 3.3377 | 1ST FLOOR UPPER | 1558 |  | 1ST FLOOR UPPER | 1290
| SB17 | 0 | 0 | 0 | 0 | 0 | 1 | 100 |  | 0.64935 | 0 | 1ST FLOOR LOWER | 1513 |  | 1ST FLOOR LOWER | 1090
| SB5 | 0 | 1 | 1 | 0 | 0 | 1 | 169 |  | 1.0974 | 0 | GROUND FLOOR | 1626 |  | GROUND FLOOR | 1322
| SB6 | 0 | 0 | 0 | 0 | 1 | 1 | 150 |  | 0.97403 | 0
| SB7 | 0 | 0 | 1 | 0 | 0 | 1 | 145 |  | 0.94156 | 0
| SB19 | 0 | 1 | 0 | 0 | 0 | 1 | 124 | 443 | 0.80519 | 2.8766
| SB12 | 1 | 0 | 0 | 1 | 0 | 1 | 220 |  | 1.4286 | 0
| SB11 | 0 | 1 | 0 | 0 | 1 | 1 | 174 | 419 | 1.1299 | 2.7208
| SB16 | [5 empty] | 1 | 100 | 290 | 0.64935 | 1.8831
| SB9 |  |  |  | 2 | 1 | 1 | 190 |  | 1.2338 | 0
| SB10 |  |  | 1 |  |  | 1 | 145 |  | 0.94156 | 0
| SB14 | 1 |  | 1 | 1 |  | 1 | 265 |  | 1.7208 | 0
| SB1 | 1 | 1 | 1 | 1 |  | 1 | 289 | 539 | 1.8766 | 3.5
| SB2 |  |  |  |  | 1 | 1 | 150 | 250 | 0.97403 | 1.6234
| SB15 | [5 empty] | 1 | 100 |  | 0.64935 | 0
| SB8 | 1 |  | 1 | 1 |  | 1 | 265 |  | 1.7208 | 0
| SB18 | [5 empty] | 1 | 100 |  | 0.64935 | 0
0
0
| 16 | [9 empty] | 0
|  | Fan | CL | TL | LB | EF | SS |  |  |  | 0
| ESB3 | [5 empty] | 1 | 100 |  | 0.64935 | 0
| ESB4 | 1 |  | 1 | 1 |  | 1 | 265 | 365 | 1.7208 | 2.3701
| ESB5 | 1 |  |  | 1 |  | 1 | 220 |  | 1.4286 | 0
| ESB6 |  |  |  | 1 |  | 1 | 120 |  | 0.77922 | 0
| ESB7 | 1 |  |  |  |  | 1 | 200 |  | 1.2987 | 0
| ESB19 |  | 1 |  |  |  | 1 | 124 | 464 | 0.80519 | 3.013
| ESB12 |  |  | 1 |  |  | 1 | 145 |  | 0.94156 | 0
| ESB11 |  |  |  | 1 |  | 1 | 120 | 320 | 0.77922 | 2.0779
| ESB9 | 1 |  |  | 1 |  | 1 | 220 |  | 1.4286 | 0
| ESB8 |  |  |  | 1 |  | 1 | 120 |  | 0.77922 | 0
| ESB10 | 1 |  | 1 |  |  | 1 | 245 |  | 1.5909 | 0
| ESB14 | 1 |  | 1 | 1 |  | 1 | 265 |  | 1.7208 | 0
| ESB1 | [5 empty] | 1 | 100 | 340 | 0.64935 | 2.2078
| ESB2 | 1 |  |  | 2 |  | 1 | 240 |  | 1.5584 | 0
0
0
| 13 | [9 empty] | 0
| 1ST FLOOR (UPPER) | [9 empty] | 0
|  | F | CL | TL | LB | EF | SS |  |  |  | 0
| SB7 | [5 empty] | 1 | 100 |  | 0.64935 | 0 | Top floor
| SB8 | 1 | 1 | 1 | 1 | 1 | 1 | 339 | 539 | 2.2013 | 3.5 |  | total SB (W) | ST socket (number) | S socket (number) | Power | current
| SB18 | [5 empty] | 1 | 100 |  | 0.64935 | 0 | SDB4 | 3100 | 1 | 7 | 8420 | 54.6753
| SB9 |  | 1 | 1 |  |  | 1 | 169 |  | 1.0974 | 0 | ESDB4 | 2484 | 6 | 0 | 7738.8 | 50.2519
| SB12 |  |  | 1 |  |  | 1 | 145 | 314 | 0.94156 | 2.039
| SB13 |  |  |  |  | 1 | 1 | 150 |  | 0.97403 | 0 | First Floor Upper
| SB19 | [5 empty] | 1 | 100 | 250 | 0.64935 | 1.6234
| SB11 |  |  |  | 2 | 1 | 1 | 190 | 440 | 1.2338 | 2.8571 | SDB3 | 1558 | 1 | 5 | 5840.6 | 37.926
| SB10 | 1 |  | 1 | 1 |  | 1 | 265 |  | 1.7208 | 0 | ESDB3 | 1290 | 5 | 0 | 5903 | 38.3312
0
[11 empty] | 0 | First Floor Lower
| ESB7 | 1 |  |  | 1 |  | 1 | 220 |  | 1.4286 | 0 | SDB2 | 1513 | 2 | 3 | 5309.1 | 34.4747
| ESB8 |  |  |  | 1 |  | 1 | 120 | 340 | 0.77922 | 2.2078 | ESDB2 | 1090 | 4 | 0 | 4763 | 30.9286
| ESB9 | 1 |  |  | 1 |  | 1 | 220 |  | 1.4286 | 0
| ESB12 | [5 empty] | 1 | 100 | 320 | 0.64935 | 2.0779 | Ground Floor
| ESB13 |  |  |  | 1 |  | 1 | 120 |  | 0.77922 | 0 | SDB1 | 1626 | 1 | 0 | 2138.2 | 13.8844
| ESB11 | 1 |  | 1 |  |  | 1 | 245 | 365 | 1.5909 | 2.3701 | ESDB1 | 1322 | 1 | 0 | 1925.4 | 12.5026
| ESB10 | 1 |  | 1 | 1 |  | 1 | 265 |  | 1.7208 | 0
0
0
0
| 1ST FLOOR (LOWER) | [9 empty] | 0 |  |  |  | pf due to PFI plant | 0.95
|  | F | CL | TL | LB | EF | SS |  |  |  | 0 | Total SDB | 21707.9
[11 empty] | 0 | Total ESDB | 20330.2
| SB3 | 1 | 1 |  | 2 |  | 1 | 264 |  | 1.7143 | 0 | EMDB load | 14231.14
| SB1 | 1 | 1 | 1 |  |  | 1 | 269 | 689 | 1.7468 | 4.474 | EMDB current | 30.8033
| SB2 |  |  |  | 1 | 1 | 1 | 170 | 420 | 1.1039 | 2.7273 | pump load | 5000
| SB16 | [5 empty] | 1 | 100 |  | 0.64935 | 0 | MDB load | 28657.328
| SB14 |  |  |  |  | 1 | 1 | 150 |  | 0.97403 | 0 | MDB current | 45.7055
| SB4 |  |  | 1 | 1 |  | 1 | 165 |  | 1.0714 | 0
| SB6 | 1 |  | 1 |  | 1 | 1 | 295 |  | 1.9156 | 0
| SB17 | [5 empty] | 1 | 100 | 395 | 0.64935 | 2.5649
0
0
|  | F | CL | TL | LB | EF | SS |  |  |  | 0
0
| ESB3 | 1 |  | 1 |  |  | 1 | 245 |  | 1.5909 | 0
| ESB1 | 1 |  |  | 1 |  | 1 | 220 | 460 | 1.4286 | 2.987
| ESB2 |  |  |  | 1 |  | 1 | 120 | 240 | 0.77922 | 1.5584 | Calculation for PFI Plant
| ESB14 |  |  |  | 1 |  | 1 | 120 |  | 0.77922 | 0 | cos x | 0.7
| ESB4 | 1 |  | 1 |  |  | 1 | 245 |  | 1.5909 | 0 | sin x | 0.71414
| ESB6 |  |  |  | 2 |  | 1 | 140 |  | 0.90909 | 0 | tan x | 1.0202
[11 empty] | 0 | Q = Ptan x | 29236.3224
[11 empty] | 0 | After PFI improvement
| GROUND | [9 empty] | 0 | I | 44.2975
|  | F | CL | TL | LB | EF | SS |  |  |  | 0
| SB2 |  | 1 |  |  |  | 1 | 124 |  | 0.80519 | 0
| SB1 | 1 | 2 | 1 |  |  | 1 | 293 | 417 | 1.9026 | 2.7078
| SB3 |  | 3 | 1 |  |  | 1 | 217 |  | 1.4091 | 0 | Transformer Calculation
| SB5 |  | 1 | 2 |  |  | 1 | 214 | 431 | 1.3896 | 2.7987 | S = 3VI | 30165.6084
| SB4 |  |  | 1 |  | 2 | 1 | 245 |  | 1.5909 | 0
| SB7 |  |  |  |  | 1 | 0 | 50 | 220 | 0.32468 | 1.4286
| SB6 |  |  |  | 1 | 1 | 1 | 170 |  | 1.1039 | 0
| SB20 (Lobby) |  | 1 |  | 1 |  | 1 | 144 |  | 0.93506 | 0
| SB15 (LOBBY) |  | 1 | 1 |  |  | 1 | 169 |  | 1.0974 | 0
|  | F | CL | TL | LB | EF | SS |  |  |  | 0
| ESB2 | 1 | 2 |  | 1 |  | 1 | 268 |  | 1.7403 | 0
| ESB1 |  | 2 |  |  |  | 1 | 148 | 416 | 0.96104 | 2.7013
| ESB3 |  | 1 |  |  |  | 1 | 124 |  | 0.80519 | 0
| ESB5 |  | 1 |  |  |  | 1 | 124 | 248 | 0.80519 | 1.6104
| ESB4 |  |  | 1 |  |  | 1 | 145 |  | 0.94156 | 0
| ESB7 |  |  |  | 1 |  | 0 | 20 | 265 | 0.12987 | 1.7208
| ESB6 | 1 |  | 1 |  |  | 1 | 245 |  | 1.5909 | 0
| ESB20 (Lobby) |  | 1 |  |  |  | 1 | 124 |  | 0.80519 | 0
| ESB15(LOBBY) |  | 1 |  |  |  | 1 | 124 |  | 0.80519 | 0
1st floor Upper
|  | F | CL | TL | LB | EF | SS
| SB7 | [5 empty] | 1 | SS12
| SB8 | 1 | 1 | 1 | 1 | 1 | 1 | F7, TL6,
| SB18 | [5 empty] | 1
| SB9 |  | 1 | 1 |  |  | 1
| SB12 |  |  | 1 |  |  | 1
| SB13 |  |  |  |  | 1 | 1
| SB19 | [5 empty] | 1
| SB11 |  |  |  | 2 | 1 | 1
| SB10 | 1 |  | 1 | 1 |  | 1
|  | F | CL | TL | LB | EF | SS
| ESB7 | 1 |  |  | 1 |  | 1
| ESB8 |  |  |  | 1 |  | 1
| ESB9 | 1 |  |  | 1 |  | 1
| ESB12 | [5 empty] | 1
| ESB13 |  |  |  | 1 |  | 1
| ESB11 | 1 |  | 1 |  |  | 1
| ESB10 | 1 |  | 1 | 1 |  | 1